## Firesafety codes chekcing
prompt | Completion
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 1.14 A design that relies on an unrealistic or unsustainable management regime cannot be considered to have met the requirements of the Building Regulations. -Building design specification clause: The design for the project is based on relevant sustainable management regime regulations, and all the requirements are met in pratical. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 1.14 A design that relies on an unrealistic or unsustainable management regime cannot be considered to have met the requirements of the Building Regulations. -Building design specification clause: The design for the project is highly based on relevant sustainable management regime regulations, though some excepions coming with are explained in following content. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 1.14 A design that relies on an unrealistic or unsustainable management regime cannot be considered to have met the requirements of the Building Regulations. -Building design specification clause: The project's design is guided by the regulations of the applicable sustainable management regime, and all criteria are really satisfied. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 1.14 A design that relies on an unrealistic or unsustainable management regime cannot be considered to have met the requirements of the Building Regulations. -Building design specification clause: The project's design is based on appropriate sustainable management regime standards, and all criteria are really satisfied. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 1.15 It is therefore essential that the design team have a full understanding of the type of care being provided and the dependency of the patients, and that the client team fully appreciate the constraints imposed by the design on the movement and evacuation of patients, visitors and staff. The design team and approving authorities should not assume that a design which complies with the requirements in this document will be safe: it needs to be supported by a fully developed emergency plan. This is also a legal requirement imposed by the Fire Safety Order. -Building design specification clause: The design team has fully communicated with the representative of the client team about the evacuation plans for all kinds of characters, i.e. patients, visitors and staff etc. to guarantee the effect. The emergency evacuation plan has been made, and termly rehearsal is suggested for all characters in the project hospital to met the requiremetns of Fire Safety Order. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 1.15 It is therefore essential that the design team have a full understanding of the type of care being provided and the dependency of the patients, and that the client team fully appreciate the constraints imposed by the design on the movement and evacuation of patients, visitors and staff. The design team and approving authorities should not assume that a design which complies with the requirements in this document will be safe: it needs to be supported by a fully developed emergency plan. This is also a legal requirement imposed by the Fire Safety Order. -Building design specification clause: To ensure the desired outcome, the design team has had extensive communication with the client team representative on the evacuation plans for all types of characters, including patients, visitors, employees, and others. The emergency evacuation plan has been created, and it is advised that everyone playing a part in the project hospital rehearses on a regular basis to comply with the Fire Safety Order requirements. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 1.15 It is therefore essential that the design team have a full understanding of the type of care being provided and the dependency of the patients, and that the client team fully appreciate the constraints imposed by the design on the movement and evacuation of patients, visitors and staff. The design team and approving authorities should not assume that a design which complies with the requirements in this document will be safe: it needs to be supported by a fully developed emergency plan. This is also a legal requirement imposed by the Fire Safety Order. -Building design specification clause: To ensure the effect, the design team has completely discussed the evacuation plans with the client team representative for all types of characters, including patients, visitors, personnel, etc. In order to comply with the requirements of the Fire Safety Order, the emergency evacuation plan has been created, and it is advised that all characters in the project hospital practise it on a regular basis. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 1.15 It is therefore essential that the design team have a full understanding of the type of care being provided and the dependency of the patients, and that the client team fully appreciate the constraints imposed by the design on the movement and evacuation of patients, visitors and staff. The design team and approving authorities should not assume that a design which complies with the requirements in this document will be safe: it needs to be supported by a fully developed emergency plan. This is also a legal requirement imposed by the Fire Safety Order. -Building design specification clause: The emergency plans are developed under the fully communications with the clients representatives, though there are some sections of the deisgn may not completely meet the requirements will be modified in further discussions. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 1.16 The preparation of the emergency evacuation plan commences during the design phase and should be developed through the user consultation process. It is important to stress that in relation to the design of appropriate fire precautions, each type of clinical service will present its own unique set of problems which will only fully emerge during the design phase. It is therefore essential that architects and designers, through the client user group consultation process, fully understand and record the fire safety issues associated with the clinical service being provided and the patients being treated. -Building design specification clause: The preparation of the emergency evacuation plan begins with the design of the project. The design team has full communication with the representative of the client to understand all types of unique clinical service. Then the corresponding emergency evacuation plan is developed to met the requirements from the client hospital. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 1.16 The preparation of the emergency evacuation plan commences during the design phase and should be developed through the user consultation process. It is important to stress that in relation to the design of appropriate fire precautions, each type of clinical service will present its own unique set of problems which will only fully emerge during the design phase. It is therefore essential that architects and designers, through the client user group consultation process, fully understand and record the fire safety issues associated with the clinical service being provided and the patients being treated. -Building design specification clause: The emergency evacuation plans are sorted out after the fully communications with the clients representatives to understand all the unique problems of all types of clinical services, though some of special requirements which may not be met during the implementation progress will be modified in fruther discussions. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-1.16 The preparation of the emergency evacuation plan commences during the design phase and should be developed through the user consultation process. It is important to stress that in relation to the design of appropriate fire precautions, each type of clinical service will present its own unique set of problems which will only fully emerge during the design phase. It is therefore essential that architects and designers, through the client user group consultation process, fully understand and record the fire safety issues associated with the clinical service being provided and the patients being treated. -Building design specification clause: The project's design serves as the foundation for creating the emergency evacuation strategy. The design team is in constant contact with the client's representative in order to fully comprehend the many forms of distinct therapeutic services. Finally, in accordance with the demands of the client hospital, a matching emergency evacuation plan is created. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 1.16 The preparation of the emergency evacuation plan commences during the design phase and should be developed through the user consultation process. It is important to stress that in relation to the design of appropriate fire precautions, each type of clinical service will present its own unique set of problems which will only fully emerge during the design phase. It is therefore essential that architects and designers, through the client user group consultation process, fully understand and record the fire safety issues associated with the clinical service being provided and the patients being treated. -Building design specification clause: Designing the project is the first step in creating the emergency evacuation plan. The design team is in constant contact with the client's representative to fully comprehend every kind of special therapeutic service. After the client hospital's needs have been completed, a related emergency evacuation plan is created. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 1.17 The fire safety measures and the emergency evacuation strategy should be developed and agreed through discussions with: a. Client user group - generally involving clinicians, nurses, managers, the fire safety advisor and the local security management specialist;b. Design team - architects and engineers;c. Fire service representative; and d. Building control or approved inspector. -Building design specification clause: The fire safety measures and the emergency evacuation strategy are developed with the following objects agreement through discussion: "a. Client user group including clinicians, nurses, managers, the fire safety advisor and local security management specialist; b. Design team - architecture and engineers; c. Five service representative; and d. Building control or approved inspector." | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 1.17 The fire safety measures and the emergency evacuation strategy should be developed and agreed through discussions with: a. Client user group - generally involving clinicians, nurses, managers, the fire safety advisor and the local security management specialist;b. Design team - architects and engineers;c. Fire service representative; and d. Building control or approved inspector. -Building design specification clause: The fire safety measures and the emergency evacuation strategy are developed based on the typical project experience with the permission of representatives of the clients." | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 1.17 The fire safety measures and the emergency evacuation strategy should be developed and agreed through discussions with: a. Client user group - generally involving clinicians, nurses, managers, the fire safety advisor and the local security management specialist;b. Design team - architects and engineers;c. Fire service representative; and d. Building control or approved inspector. -Building design specification clause: The following groups are involved in developing the emergency evacuation plan and fire safety measures: "a. Client user group, which includes clinicians, nurses, managers, the fire safety advisor, and local security management specialist; b. Design team, which includes architects and engineers; c. Five service representatives; and d. Building control or approved inspector." | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 1.17 The fire safety measures and the emergency evacuation strategy should be developed and agreed through discussions with: a. Client user group - generally involving clinicians, nurses, managers, the fire safety advisor and the local security management specialist;b. Design team - architects and engineers;c. Fire service representative; and d. Building control or approved inspector. -Building design specification clause: The following groups are involved in developing the emergency evacuation plan and fire safety measures: "a. Client user group, which consists of clinicians, nurses, managers, the fire safety advisor, and local security management specialist; b. Design team, which includes architects and engineers; c. Five service representatives; and d. Building control or approved inspector." | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 1.19 The outcome of these discussions will be all the information required to support Regulation 38 and should include:a. the emergency evacuation plan including all assumptions in relation to:(i) theavailability of adequately trained staff to manage an evacuation;(ii) the design of the fire safety systems (such as fire load);(iii) any risk assessments or risk analysis; b. all assumptions in the design of the fire safety arrangements regarding the management of the building; c. escape routes (including stairs and lifts), escape strategy (for example simultaneous or phased) and muster points; d. details of all fire safety measures, including (but not exhaustively):(i) compartmentation, cavity barriers, fire doors, self-closing fire doors and other doors equipped with relevant hardware (for example electronic security locks), and fire and smoke dampers;(ii) automatic fire detection systems, emergency communication systems, CCTV, fire safety signage, emergency lighting, fire extinguishers;(iii) dry or wet risers and other firefighting equipment, other interior facilities for the fire-and-rescue service, emergency control rooms, location of hydrants outside the building, and other exterior facilities for the fire-and-rescue service;(iv) sprinkler system(s) design, including isolating valves and control equipment; and(v) smoke-control system(s) (or HVAC system with a smoke-control function) design, including mode of operation and control systems;e. any high-risk areas (for example heating machinery) and particular hazards; f. as-built plans of the building showing the locations of the above;g. specifications of any fire safety equipment provided, including operational details, operator manuals, software, system zoning, routine inspection, and testing and maintenance schedules, together with records of any acceptance or commissioning tests;h. any other details appropriate for the specific building; and i. for large and/or complex premises, the findings of the QDR. -Building design specification clause: The evacuation plan with all agreements contains the following content: a. the emergency evacuation plan is developed with the assumptions of: "(i) theavailability of adequately trained staff to manage an evacuation;(ii) the design of the fire safety systems (such as fire load);(iii) any risk assessments or risk analysis;" b. b. all assumptions in the design of the fire safety arrangements regarding the management of the building; c. escape routes (including stairs and lifts), escape strategy (for example simultaneous or phased) and muster points; d. details of all fire safety measures, including (but not exhaustively):(i) compartmentation, cavity barriers, fire doors, self-closing fire doors and other doors equipped with relevant hardware (for example electronic security locks), and fire and smoke dampers;(ii) automatic fire detection systems, emergency communication systems, CCTV, fire safety signage, emergency lighting, fire extinguishers;(iii) dry or wet risers and other firefighting equipment, other interior facilities for the fire-and-rescue service, emergency control rooms, location of hydrants outside the building, and other exterior facilities for the fire-and-rescue service;(iv) sprinkler system(s) design, including isolating valves and control equipment; and(v) smoke-control system(s) (or HVAC system with a smoke-control function) design, including mode of operation and control systems;e. any high-risk areas (for example heating machinery) and particular hazards; f. as-built plans of the building showing the locations of the above;g. specifications of any fire safety equipment provided, including operational details, operator manuals, software, system zoning, routine inspection, and testing and maintenance schedules, together with records of any acceptance or commissioning tests;h. any other details appropriate for the specific building; and i. for large and/or complex premises, the findings of the QDR. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 1.25 A significant number of fires occur as a result of certain building activities. The site conduct of contractors should be adequately supervised and controlled. Adequate precautions against fire should be in place, and regular contact with contractors should be maintained to ensure that local fire safety policies are being complied with. -Building design specification clause: The site conduct of contractors requires adequately supervised and conteolled. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 1.25 A significant number of fires occur as a result of certain building activities. The site conduct of contractors should be adequately supervised and controlled. Adequate precautions against fire should be in place, and regular contact with contractors should be maintained to ensure that local fire safety policies are being complied with. -Building design specification clause: The site conduct of contractors are partially supervised and conteolled. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 1.25 A significant number of fires occur as a result of certain building activities. The site conduct of contractors should be adequately supervised and controlled. Adequate precautions against fire should be in place, and regular contact with contractors should be maintained to ensure that local fire safety policies are being complied with. -Building design specification clause: Contractor behaviour on the job site needs to be properly supervised and controlled. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 1.25 A significant number of fires occur as a result of certain building activities. The site conduct of contractors should be adequately supervised and controlled. Adequate precautions against fire should be in place, and regular contact with contractors should be maintained to ensure that local fire safety policies are being complied with. -Building design specification clause: The behaviour of contractors on the job site needs to be properly controlled and overseen. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 1.26 It is also important to ensure that - C when new buildings are being constructed and handed over in phases - C due consideration is given to fire safety after handover. There must be no conflict in the operation of the alarm and detection system between the healthcareoccupied part of the premises and the construction area. Of equal importance is the need to ensure that means of escape is readily available at all times. -Building design specification clause: All the fire safety systems are tested before hand over, including fire alarm systems, emergent evacuation infrastructures and plans. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 1.26 It is also important to ensure that - C when new buildings are being constructed and handed over in phases - C due consideration is given to fire safety after handover. There must be no conflict in the operation of the alarm and detection system between the healthcareoccupied part of the premises and the construction area. Of equal importance is the need to ensure that means of escape is readily available at all times. -Building design specification clause: Most of the fire safety systems are tested before hand over, the rest of the tests will be completed in the future. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.17 In healthcare premises, the practice of designating certain stairways as escape stairways and others as accommodation stairways only is not acceptable, since in an emergency any stairway will be used if necessary. Therefore all stairways should be designed as escape stairways other than those contained wholly within and only serving an atrium. -Building design specification clause: In this project, all stairways are designed as escape stairways for emergency use. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.17 In healthcare premises, the practice of designating certain stairways as escape stairways and others as accommodation stairways only is not acceptable, since in an emergency any stairway will be used if necessary. Therefore all stairways should be designed as escape stairways other than those contained wholly within and only serving an atrium. -Building design specification clause: In this project, most of stairways are designed as escape stairways for emergency use. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.24 In operating theatres and areas that provide intensive care, any movement or evacuation of patients may be life-threatening; consequently, additional precautions are required to address the implications of: a. fire and smoke in a compartment either adjacent or below; b. fire and smoke within the department itself. -Building design specification clause: Mechanical smoke exhaust systems and portable carbon dioxide fire extinguishers are set in the following area: a. operating theatres; b. Intensive Care Unit; c. Evacuation corridors. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.24 In operating theatres and areas that provide intensive care, any movement or evacuation of patients may be life-threatening; consequently, additional precautions are required to address the implications of: a. fire and smoke in a compartment either adjacent or below; b. fire and smoke within the department itself. -Building design specification clause: Mechanical smoke exhaust systems and portable carbon dioxide fire extinguishers are set in the following area: a. operating theatres; b. Intensive Care Unit. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.24 In operating theatres and areas that provide intensive care, any movement or evacuation of patients may be life-threatening; consequently, additional precautions are required to address the implications of: a. fire and smoke in a compartment either adjacent or below; b. fire and smoke within the department itself. -Building design specification clause: Natural smoke exhaust systems and portable carbon dioxide fire extinguishers are set in the following area: a. operating theatres; b. Intensive Care Unit; c. Evacuation corridors. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.27 The aim of any design should be to prevent a fire in an adjacent compartment either on the same storey or on a storey above or below, requiring the evacuation of a intensive care area. The compartmentation and HVAC (heating, ventilation and air-conditioning) systems should be designed so that an adequate period of time is provided to enable a fire to be detected and extinguished before it threatens occupants. -Building design specification clause: The mechanical smoke exhaust system is set for fire component A-1F-1, 4 smoke control zones are set for the component, ceiling screens are applied to divide the smoke control zones. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.27 The aim of any design should be to prevent a fire in an adjacent compartment either on the same storey or on a storey above or below, requiring the evacuation of a intensive care area. The compartmentation and HVAC (heating, ventilation and air-conditioning) systems should be designed so that an adequate period of time is provided to enable a fire to be detected and extinguished before it threatens occupants. -Building design specification clause: HVAC systems for fire-safety are not mentioned in this design. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.28 The HVAC systems provided to intensive care areas are designed so that the pressure within the department is maintained at slightly above that of the adjacent areas. In a fire emergency, the continuing operation of these systems will assist in preventing smoke and other products of combustion entering the intensive care area. -Building design specification clause: An independent fresh air system with an air filter device is set for each intensive care area. The fresh air system should keep a positive pressure environment. In a fire emergency, the continuing operation of these systems will assist in preventing smoke and other products of combustion entering the intensive care area. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.28 The HVAC systems provided to intensive care areas are designed so that the pressure within the department is maintained at slightly above that of the adjacent areas. In a fire emergency, the continuing operation of these systems will assist in preventing smoke and other products of combustion entering the intensive care area. -Building design specification clause: HVAC systems for smoke preventing are not included in this design. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.30 Protected lobbies are provided to those areas of the premises that require additional means to protect against the movement of smoke. Where risk assessment has demonstrated a need, very high dependency treatment areas should be provided with a lobby, which should be sized appropriately to fully accommodate a bed, the associated ancillary equipment and nursing staff, and should include sufficient additional floor space to allow for any manoeuvring as necessary. -Building design specification clause: Protected lobbies are set for the intensive care area in this project, which should be sized appropriately to fully accommodate a bed, the associated ancillary equipment and nursing staff, and should include sufficient additional floor space to allow for any manoeuvring as necessary. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.30 Protected lobbies are provided to those areas of the premises that require additional means to protect against the movement of smoke. Where risk assessment has demonstrated a need, very high dependency treatment areas should be provided with a lobby, which should be sized appropriately to fully accommodate a bed, the associated ancillary equipment and nursing staff, and should include sufficient additional floor space to allow for any manoeuvring as necessary. -Building design specification clause: Most of protected lobbies are set for the intensive care area in this project, which should be sized appropriately to fully accommodate a bed, the associated ancillary equipment and nursing staff, and should include sufficient additional floor space to allow for any manoeuvring as necessary. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.31 Where smoke movement into an area accommodating very high dependency patients has been identified as a potential risk (that is, where no hospital streets have been provided), every door opening in the compartment wall should be provided with a protected lobby, each door of which will provide a minimum period of fire resistance of 30 minutes. -Building design specification clause: Lobby rooms are set before accessing into high dependency patient rooms to prevent smoke, the door opening in the component wall should have a minimum period of 30 minutes of fire resistance. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.31 Where smoke movement into an area accommodating very high dependency patients has been identified as a potential risk (that is, where no hospital streets have been provided), every door opening in the compartment wall should be provided with a protected lobby, each door of which will provide a minimum period of fire resistance of 30 minutes. -Building design specification clause: In most situations before accessing into high dependency patients rooms, lobby rooms are et to prevent smoke, the door opening in the component wall should have a minimum period of 30 minutes of fire resistance. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.34 In many cases the use of an anaesthetic will restrict mobility so that patients will require assistance to escape in the event of a fire. Therefore in DTS and DSS premises the means of escape from relevant areas should be designed so that it is always possible, in the first instance, to escape: a. horizontally to a place of relative safety from where further horizontal or vertical evacuation is possible; or b. directly to a place of safety at ground level. -Building design specification clause: In this project, DTS and DSS rooms are set on the ground floor and close to the emergency exit so the patients can escape with help in a dangerous situation. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.34 In many cases the use of an anaesthetic will restrict mobility so that patients will require assistance to escape in the event of a fire. Therefore in DTS and DSS premises the means of escape from relevant areas should be designed so that it is always possible, in the first instance, to escape: a. horizontally to a place of relative safety from where further horizontal or vertical evacuation is possible; or b. directly to a place of safety at ground level. -Building design specification clause: In this project, DTS and DSS rooms are set at the end of the evacuation corridor. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.35 The place of relative safety should either be a separate 30 minute sub-compartment, or a refuge in an escape stairway that is enclosed in 30 minute fire-resisting construction, either of which should be large enough to accommodate the number of patients who at any one time could reasonably be expected to be receiving or recovering from minor invasive investigations or procedures. -Building design specification clause: Lobby rooms, and escape stairways should either have minimum period of 30 minutes fire resistance, and enough area to accommodate the number of patients who at any one time could reasonably be expected to be receiving or recovering from minor invasive investigations or procedures. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.35 The place of relative safety should either be a separate 30 minute sub-compartment, or a refuge in an escape stairway that is enclosed in 30 minute fire-resisting construction, either of which should be large enough to accommodate the number of patients who at any one time could reasonably be expected to be receiving or recovering from minor invasive investigations or procedures. -Building design specification clause: Lobby rooms, and escape stairways should either have no minimum period requirements for fire resistance, and enough area to accommodate the number of patients who at any one time could reasonably be expected to be receiving or recovering from minor invasive investigations or procedures. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.43 Should a fire start, it will be necessary to evacuate the sub-compartment of fire origin and the number of staff available will influence the speed of evacuation. Such evacuation may be progressive horizontal evacuation to other compartments or sub-compartments as described in Chapter 3. -Building design specification clause: The progressive horizontal evacuation plan is applied for sub-compartment of fire origin in this project. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.43 Should a fire start, it will be necessary to evacuate the sub-compartment of fire origin and the number of staff available will influence the speed of evacuation. Such evacuation may be progressive horizontal evacuation to other compartments or sub-compartments as described in Chapter 3. -Building design specification clause: The progressive horizontal evacuation plan is not included in this project. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.46 The potential to configure the alarm and detection system such that in the first instance only staff receive the alarm, can reduce adverse reactions from patients. A general alarm confined to the compartment or zone would only be activated as the evacuation strategy was implemented. Further guidance is provided in HTM 05-03 Part B. -Building design specification clause: Fire detection and alarm systems are set in this project. The alarm would be sent to security first, and the general alarm is activated after verification by security to implement the evacuation strategy. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.46 The potential to configure the alarm and detection system such that in the first instance only staff receive the alarm, can reduce adverse reactions from patients. A general alarm confined to the compartment or zone would only be activated as the evacuation strategy was implemented. Further guidance is provided in HTM 05-03 Part B. -Building design specification clause: Fire detection and alarm systems are not included in this project. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.47 Integration of the alarm and detection system with staff and patient monitoring and location systems can improve response times to alarm situations. -Building design specification clause: The alarm and detection system is integrated with staff and patient monitoring and location system in this project to improve emergency reaction efficiency. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.47 Integration of the alarm and detection system with staff and patient monitoring and location systems can improve response times to alarm situations. -Building design specification clause: The alarm and detection system is not included in this project. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.48 For security purposes, it is important that final exits do not release immediately on actuation of the alarm. The release mechanism should form part of the overall strategy for managing the evacuation. This gives control to the staff and increases the security of the facility. Some means of control should be provided such that these doors can be opened by staff, on confirmation of the fire signal, when it becomes necessary to evacuate to a designated (secure) assembly point. -Building design specification clause: The final exists should be opened automatically in sequence of evacuation strategy to keep the strategy safe and effect, though all of these exists can be opened manually in case of few exceptions. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.48 For security purposes, it is important that final exits do not release immediately on actuation of the alarm. The release mechanism should form part of the overall strategy for managing the evacuation. This gives control to the staff and increases the security of the facility. Some means of control should be provided such that these doors can be opened by staff, on confirmation of the fire signal, when it becomes necessary to evacuate to a designated (secure) assembly point. -Building design specification clause: Aall of evacuation exists can be opened manually in case of few exceptions. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.49 Should it become necessary to evacuate an entire facility or part thereof, adequate safe and secure external assembly points should be available. -Building design specification clause: There are 5 assembly points set in the project to keep the entire building evacuating available. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.49 Should it become necessary to evacuate an entire facility or part thereof, adequate safe and secure external assembly points should be available. -Building design specification clause: Assembly points are not given in this project. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.52 Sleeping accommodation should be in a separate compartment from day facilities. -Building design specification clause: Sleeping accommodation is set separately compartment from day facilities. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.52 Sleeping accommodation should be in a separate compartment from day facilities. -Building design specification clause: Sleeping accommodation is set in the same compartment with day facilities. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.53 Accommodation in compartments providing sleeping accommodation should be limited to: a. bedrooms;b. bathrooms, WCs etc; c. cleaners' room; d. a small office for staff on overnight duty (this may be an office or a recess off a circulation route);e. linen stores. -Building design specification clause: Only the following rooms provide sleeping accommodation, including bedrooms, bathrooms, WCs, cleaners' rooms, overnight staff office, linen stores etc. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.53 Accommodation in compartments providing sleeping accommodation should be limited to: a. bedrooms;b. bathrooms, WCs etc; c. cleaners' room; d. a small office for staff on overnight duty (this may be an office or a recess off a circulation route);e. linen stores. -Building design specification clause: The rooms which provide sleeping accommodation are not specifically restricted. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.54 Where sleeping accommodation is segregated by sex, male and female bedrooms should be in separate sub-compartments. -Building design specification clause: Sleeping accommodation is segregated by sex. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.54 Where sleeping accommodation is segregated by sex, male and female bedrooms should be in separate sub-compartments. -Building design specification clause: Sleeping accommodation is not segregated by sex. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.55 The maximum number of beds in any sub-compartment, including swing beds, should be no more than 10. -Building design specification clause: The maximum number of beds in any room is not over 10. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.55 The maximum number of beds in any sub-compartment, including swing beds, should be no more than 10. -Building design specification clause: For some rooms, the maximum number of beds are over 10. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.56 Where "swing beds" are provided it should be possible to include the swing beds in either sub-compartment. -Building design specification clause: Swing beds can be provided in any sub-compartment in this project. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.57 Depending on the patients it may be necessary to maintain segregation during evacuation; where this is the case, the design of evacuation routes should ensure that this is always possible. This will also extend to secure places of safety away from the effects of fire, outside the building. -Building design specification clause: Independent evacuation routes are set for infectious patients to maintain segregation. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.57 Depending on the patients it may be necessary to maintain segregation during evacuation; where this is the case, the design of evacuation routes should ensure that this is always possible. This will also extend to secure places of safety away from the effects of fire, outside the building. -Building design specification clause: Infectious patients evacuation routes are set together with other people in the building to maintain segregation. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.58 Bedrooms:a. All bedrooms should be classed as fire hazard rooms.b. It may be necessary to provide the potential for bedroom doors to be locked from the inside. However, if this is required, they should be easy to open from the inside without recourse to a key. In addition, any locking device used should be easy to open from the outside of the room by means of a standard key issued to all staff. -Building design specification clause: Bedrooms: a. All bedrooms are classed as fire hazard rooms. b. doors of the bedroom is easy to be opened from the inside without a key, in addition, the doors are easy to be opened from the outside of the room by a standard key issued to all staff. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.58 Bedrooms:a. All bedrooms should be classed as fire hazard rooms.b. It may be necessary to provide the potential for bedroom doors to be locked from the inside. However, if this is required, they should be easy to open from the inside without recourse to a key. In addition, any locking device used should be easy to open from the outside of the room by means of a standard key issued to all staff. -Building design specification clause: Bedrooms: a. Most of the bedrooms are classed as fire hazard rooms. b. doors of the bedroom is easy to be opened from the inside without a key. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.59 Where communal bathrooms are provided, these should be designed as fire hazard rooms. -Building design specification clause: Commercial bathrooms are designed as fire harzard rooms in this project. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 2.59 Where communal bathrooms are provided, these should be designed as fire hazard rooms. -Building design specification clause: Most of the commercial bathrooms are designed as fire harzard rooms in this project, the rest of the commercial bathrooms which are not designed as fire harzard rooms are explained in following context. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.1 The design and construction of the building should ensure that fires are detected at the earliest possible opportunity and that suitable warning is then given to the occupants and the emergency services. -Building design specification clause: Fire detection and alarm systems are set in this project. The alarm would be sent to security first, and the general alarm is activated after verification by security to implement the evacuation strategy. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.1 The design and construction of the building should ensure that fires are detected at the earliest possible opportunity and that suitable warning is then given to the occupants and the emergency services. -Building design specification clause: Fire detection and alarm systems are not included in this project. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.2 The provision of adequate means for detecting a fire and raising the alarm is of vital importance. Early detection permits time for orderly evacuation and allows the fire to be tackled at an earlier stage, thus minimising the damage caused. Detection is dependent on both staff observation and the automatic detection and alarm systems. -Building design specification clause: Fire detection and alarm systems are set in this project. The alarm would be sent to security first, and the general alarm is activated after verification by security to implement the evacuation strategy. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.2 The provision of adequate means for detecting a fire and raising the alarm is of vital importance. Early detection permits time for orderly evacuation and allows the fire to be tackled at an earlier stage, thus minimising the damage caused. Detection is dependent on both staff observation and the automatic detection and alarm systems. -Building design specification clause: Fire detection and alarm systems are not included in this project. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.3 Health Technical Memorandum 05-03 Part B-C "Fire detection and alarm systems" provides general principles and technical guidance on the design, specification, installation, commissioning, testing, operation and maintenance of fire alarm systems in healthcare premises. It should be read in conjunction with BS 5839-1 and the relevant parts of BS EN 54. -Building design specification clause: The design, specification, installation, commissioning, testing, operation and maintenance of fire detection and alarm systems are based on Health Technical Memorandum 05-03 Part B-C "Fire detection and alarm systems" and in conjunction with BS 5839-1 and the relevant parts of BS EN 54 in this project. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.3 Health Technical Memorandum 05-03 Part B-C "Fire detection and alarm systems" provides general principles and technical guidance on the design, specification, installation, commissioning, testing, operation and maintenance of fire alarm systems in healthcare premises. It should be read in conjunction with BS 5839-1 and the relevant parts of BS EN 54. -Building design specification clause: The design, specification, installation, commissioning, testing, operation and maintenance of fire detection and alarm systems are based on communications with representatives of the clients and relevant departments of the government. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.8 Every level with a floor area of less than 1000 m2 and which contains patient-access areas should:a. contain no more than 30 patients; andb. be divided into a minimum of two compartments. -Building design specification clause: The area of the hospital in this project is 4320 m2. Including ground floor 1317 m2, first floor 1317, second floor 843 m2, and third floor 843 m2. There are 3 compartments in the ground and first floor, 2 compartments in the second and third floor. Both of the second and third floor contain no more than 30 patients. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.8 Every level with a floor area of less than 1000 m2 and which contains patient-access areas should:a. contain no more than 30 patients; and b. be divided into a minimum of two compartments. -Building design specification clause: The area of the hospital in this project is 4320 m2. Including ground floor 1317 m2, first floor 1317, second floor 843 m2, and third floor 843 m2. There are 1 compartment in the ground and first floor, 1 compartment in the second and third floor. Both of the second and third floor contain no more than 30 patients. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.9 Where a compartment provides sleeping accommodation, the maximum number of beds in the compartment should be no more than 20. -Building design specification clause: Each of the compartment with sleeping accommodation provides no more than 2o beds in this project. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.9 Where a compartment provides sleeping accommodation, the maximum number of beds in the compartment should be no more than 20. -Building design specification clause: Each of the compartment with sleeping accommodation provides more than 20 beds in this project. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.10 On floors above ground-floor level where sprinklers are installed, the fire-resistance of the compartment walls may be reduced to 30 minutes (integrity and insulation), see paragraph 5.12. -Building design specification clause: All the floors above the ground floor where the sprinklers are installed, the minimum period of the fire-resistance of the compartment walls is over 30 minutes. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.10 On floors above ground-floor level where sprinklers are installed, the fire-resistance of the compartment walls may be reduced to 30 minutes (integrity and insulation), see paragraph 5.12. -Building design specification clause: Sprinklers systems are not included in this project. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.11 Every level up to 12 m above ground level that has a floor area of more than 1000 m2 and which contains patient-access areas should be divided into a minimum of three compartments. One of these compartments may be a hospital street (see paragraphs 3.37-C3.40). -Building design specification clause: Every level up to 12 m above ground level that has a floor area of more than 1000 m2 and which contains patient-access is divided into at least 3 compartments. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.11 Every level up to 12 m above ground level that has a floor area of more than 1000 m2 and which contains patient-access areas should be divided into a minimum of three compartments. One of these compartments may be a hospital street (see paragraphs 3.37-C3.40). -Building design specification clause: Every level up to 12 m above ground level that has a floor area of more than 1000 m2 and which contains patient-access is divided into 1 compartment. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.12 Where sprinklers are installed, the fireresistance of the compartment walls may be reduced to 30 minutes (integrity and insulation), see paragraph 5.12. -Building design specification clause: All the floors above the ground floor where the sprinklers are installed, the minimum period of the fire-resistance of the compartment walls is over 30 minutes. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.12 Where sprinklers are installed, the fireresistance of the compartment walls may be reduced to 30 minutes (integrity and insulation), see paragraph 5.12. -Building design specification clause: All the floors above the ground floor where the sprinklers are installed, there is no requirement to the minimum period of the fire-resistance of the compartment walls. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.13 Every level over 12 m above ground that contains patient-access areas should be divided into a minimum of four compartments. Where no hospital street is provided, each compartment should have a minimum floor area of 500 m2; where one of the compartments is a hospital street, the area of the hospital street may be less than 500 m2. -Building design specification clause: Every level over 12 m above ground that contains-access areas is divided into a minimum of four compartments. For the compartment is not hospital street, the minimum area is 500 m2. For a hospital street compartment, the minimum can be less than 500 m2. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.13 Every level over 12 m above ground that contains patient-access areas should be divided into a minimum of four compartments. Where no hospital street is provided, each compartment should have a minimum floor area of 500 m2; where one of the compartments is a hospital street, the area of the hospital street may be less than 500 m2. -Building design specification clause: Every level over 12 m above ground that contains-access areas is divided into 1 compartment. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.14 Where sprinklers are installed, the minimum floor area of each compartment required by paragraph 3.13 above may be reduced to 350 m2.-Building design specification clause: Some of the compartments where sprinklers are installed, the minimum area is above 350 m2. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.14 Where sprinklers are installed, the minimum floor area of each compartment required by paragraph 3.13 above may be reduced to 350 m2.-Building design specification clause: Some of the compartments where sprinklers are installed, and no requirements for minimum area. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.15 In a fire emergency each compartment should be capable of accommodating, in addition to its normal occupants, the designed occupancy (including all relevant life support systems) of the most highly occupied adjoining compartment. -Building design specification clause: Each compartment is capable of accommodating, in addition to its normal occupants, the designed occupancy (including all relevant lifesupport systems) of the most highly occupied adjoining compartment. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.15 In a fire emergency each compartment should be capable of accommodating, in addition to its normal occupants, the designed occupancy (including all relevant life support systems) of the most highly occupied adjoining compartment. -Building design specification clause: Most of the compartment are capable of accommodating, in addition to its normal occupants, the designed occupancy (including all relevant lifesupport systems) of the most highly occupied adjoining compartment. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.20 Where a storey is divided into three or more compartments, the exits from each compartment should be located so that there are at least two alternative exits that provide horizontal escape to adjoining but separate compartments. -Building design specification clause: For the storey is divided into three or more compartments, there are at least two alternative exists providing horizontal escape to adjoining but sepearate compartments. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.20 Where a storey is divided into three or more compartments, the exits from each compartment should be located so that there are at least two alternative exits that provide horizontal escape to adjoining but separate compartments. -Building design specification clause: For the storey is divided into three or more compartments, some compartments are provided a single exist providing horizontal escape to adjoining but sepearate compartments. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.24 The maximum size of a compartment permitted by this document - although appropriate for fire containment (see paragraph 5.11) - is nevertheless considered too large if the area contains patient-access areas. In the event of a fire, a large number of patients could be overcome by the spread of fire, smoke and toxic gases. Therefore, compartments containing patient-access areas should be divided into smaller sub-compartments to limit the number of patients who may be affected by a fire. Wherever possible, there should be a balance of patients between subcompartments. -Building design specification clause: For a compartment which has patient access is divided into smaller sub-compartments to limit the number of patients who may be affected by a fire. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.24 The maximum size of a compartment permitted by this document - although appropriate for fire containment (see paragraph 5.11) - is nevertheless considered too large if the area contains patient-access areas. In the event of a fire, a large number of patients could be overcome by the spread of fire, smoke and toxic gases. Therefore, compartments containing patient-access areas should be divided into smaller sub-compartments to limit the number of patients who may be affected by a fire. Wherever possible, there should be a balance of patients between subcompartments. -Building design specification clause: For a compartment in this project which has patient access contains the whole compartment and is not divided into smaller sub-compartments. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.25 A compartment should be subcompartmented if:a. it has a floor area greater than 750 m2; or b. it contains departments to which more than 30 patients will have access at the same time; orc. it contains sleeping accommodation for more than 30 patients. -Building design specification clause: Compartments are divided into sub-compartments in following conditions: a. it has a floor area greater than 750 m2; or b. it contains departments to which more than 30 patients will have access at the same time; orc. it contains sleeping accommodation for more than 30 patients. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.25 A compartment should be subcompartmented if:a. it has a floor area greater than 750 m2; or b. it contains departments to which more than 30 patients will have access at the same time; orc. it contains sleeping accommodation for more than 30 patients. -Building design specification clause: Compartments are not divided into sub-compartments in this project, the groud floor are is over 750 m2. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.26 Sub-compartments should be enclosed by walls having a minimum period of fire resistance of 30 minutes, which should terminate at the underside of: a. a compartment floor; or b. a roof. -Building design specification clause: Sub-compartments are enclosed by walls having a minimum period of fire resistance of 30 minutes, which terminate at the underside of: a. a compartment floor; or b. a roof. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.26 Sub-compartments should be enclosed by walls having a minimum period of fire resistance of 30 minutes, which should terminate at the underside of: a. a compartment floor; or b. a roof. -Building design specification clause: Sub-compartments are enclosed by walls though no requirements for minimum period of fire resistance, which terminate at the underside of: a. a compartment floor; or b. a roof. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.27 Each sub-compartment should be provided with a minimum of two exits to adjoining but separate compartments or sub-compartments. -Building design specification clause: Each sub-compartment is provided with a minimum of two exists to adjoining but separate compartments or sub-compartments. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.27 Each sub-compartment should be provided with a minimum of two exits to adjoining but separate compartments or sub-compartments. -Building design specification clause: Some sub-compartments are provided with an only exist to adjoining but separate compartments or sub-compartments. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.30 The maximum travel distance before there is a choice of escape routes should be no more than: a. 15 m for in-patient accommodation; or b. as specified in paragraphs 3.85-C3.87; orc. 18 m for all other parts of healthcare buildings.-Building design specification clause: The maximum distance for in-patient accommodation is 13m. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.30 The maximum travel distance before there is a choice of escape routes should be no more than: a. 15 m for in-patient accommodation; or b. as specified in paragraphs 3.85-C3.87; orc. 18 m for all other parts of healthcare buildings.-Building design specification clause: The maximum distance for in-patient accommodation is 30m. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.31 Any part of an enclosed escape route that has single direction of escape only, and exceeds 4.5 m, should be protected by 30-minute fire-resisting construction (integrity and insulation). This does not include travel within a room, but applies to "stub" corridors or a small corridor recess.-Building design specification clause: Any part of an enclosed escape route that has a single direction of escape only, and exceeds 4.5m, is protected by 30-minute fire-resisting construction (integrity and insulation). | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.31 Any part of an enclosed escape route that has single direction of escape only, and exceeds 4.5 m, should be protected by 30-minute fire-resisting construction (integrity and insulation). This does not include travel within a room, but applies to "stub" corridors or a small corridor recess.-Building design specification clause: Any part of an enclosed escape route that has a single direction of escape only, and exceeds 4.5m, is no required by fire-resisting. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.39 Stairways should be located so that the maximum travel distance from the exit of the stairway enclosure to a final exit from the hospital street is no more than 60 m. However, it should be noted that there are additional requirements for fire-and-rescue service access into hospital streets, see paragraphs 7.18-C7.20.-Building design specification clause: The maximum travel distance between the exit of the stairway enclosure and the final exit from the hospital street is at most 60m. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.39 Stairways should be located so that the maximum travel distance from the exit of the stairway enclosure to a final exit from the hospital street is no more than 60 m. However, it should be noted that there are additional requirements for fire-and-rescue service access into hospital streets, see paragraphs 7.18-C7.20.-Building design specification clause: The maximum travel distance between the exit of the stairway enclosure and the final exit from the hospital street is 63m. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.43 In the majority of healthcare premises the practice of designating certain stairways as escape stairways and others as accommodation stairways only is not acceptable, since in an emergency any stairway will be used if necessary. Therefore all stairways, other than those contained within and only serving an atrium, should be designed as escape stairways to permit vertical evacuation by the most appropriate method, see paragraphs 3.53 to 3.55.-Building design specification clause: All stairways other than those contained within and only serving an atrium in the project are designed as escape staiways to permit vertical evacuation by the most appropriate method. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.43 In the majority of healthcare premises the practice of designating certain stairways as escape stairways and others as accommodation stairways only is not acceptable, since in an emergency any stairway will be used if necessary. Therefore all stairways, other than those contained within and only serving an atrium, should be designed as escape stairways to permit vertical evacuation by the most appropriate method, see paragraphs 3.53 to 3.55.-Building design specification clause: Most of the stairways other than those contained within and only serving an atrium in the project are designed as escape staiways to permit vertical evacuation by the most appropriate method. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.59 Automatic final exit doors should be freely openable by hand under any condition, including power failure; otherwise, adjacent non-automatic outward-opening doors must be provided.-Building design specification clause: All of the automatic final exit doors are freely openable by hand under any condition, including power failure. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.59 Automatic final exit doors should be freely openable by hand under any condition, including power failure; otherwise, adjacent non-automatic outward-opening doors must be provided.-Building design specification clause: Most of the automatic final exit doors are freely openable by hand under any condition, including power failure, though there are some exceptions in the following context. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.60 Final exit doors should not be provided with a step and should open onto an area which is level for a distance of at least 1 metre.-Building design specification clause: No step is provided for the final exit doors, and the doors can be opened to a distance of at least 1 metre. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.60 Final exit doors should not be provided with a step and should open onto an area which is level for a distance of at least 1 metre.-Building design specification clause: No step is provided for the final exit doors, and the maximum opening distance of the doors in the west is 0.9 metre. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.64 The aim of any design should be to prevent a fire in an adjacent compartment either on the same storey or on a storey above or below requiring the evacuation of an intensive care area. The compartmentation and HVAC should be designed so that an adequate period of time is provided to enable a fire to be detected and extinguished before it threatens the occupants.-Building design specification clause: The aim of any design in this project is to prevent a fire in an adjacent compartment either on the same storey or below requiring the evacuation of an intensive care area. The compartmentation and HAVC are designed so that an adequate period of time is provided to enable a fire to be detected and extinguished before it threatens the occupants. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.65 With the exception of doors from a hospital street, every door opening in the compartment wall should be provided with a protected lobby, each door of which will provide a minimum period of fire resistance of 30?minutes (integrity). This arrangement will reduce the possibility of smoke ingress from a fire outside the department.-Building design specification clause: With the exception of doors from a hospital street, every door opening in the compartment wall is provided with a protected lobby, each door of which will provide a minimum period of fire resistance of 30 minutes (integrity). | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.65 With the exception of doors from a hospital street, every door opening in the compartment wall should be provided with a protected lobby, each door of which will provide a minimum period of fire resistance of 30?minutes (integrity). This arrangement will reduce the possibility of smoke ingress from a fire outside the department.-Building design specification clause: With the exception of doors from a hospital street, every door opening in the compartment wall is provided with a protected lobby, there is no requirement for each door's fire resistance period. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.67 The HVAC systems provided to intensive care areas are designed so that the pressure within the department is maintained at a level slightly above that of the adjacent areas. In a fire emergency, the continuing operation of these systems will assist in preventing smoke and other products of combustion entering the intensive care area.-Building design specification clause: The HVAC systems provided to intensive care areas are designed so that the pressure within the department is maintained at a level slightly above that of the adjacent areas. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.67 The HVAC systems provided to intensive care areas are designed so that the pressure within the department is maintained at a level slightly above that of the adjacent areas. In a fire emergency, the continuing operation of these systems will assist in preventing smoke and other products of combustion entering the intensive care area.-Building design specification clause: The HVAC systems provided to intensive care areas are designed, though there is no reuqirement for rooms air pressure. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.68 In departments providing intensive care, the HVAC systems should be designed so that they continue to operate in a fire emergency. The shutdown of these systems should be controlled from remote panels located either at the department entrance or adjacent to the main fire-alarm indicator panel.-Building design specification clause: In departments providing intensive care, the HVAC systems are designed so that they continue to operate in a fire emergency. The shutdown of these systems are controlled from remote panels located either at the department entrance or adjacent to the main fire-alarm indicator panel. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.68 In departments providing intensive care, the HVAC systems should be designed so that they continue to operate in a fire emergency. The shutdown of these systems should be controlled from remote panels located either at the department entrance or adjacent to the main fire-alarm indicator panel.-Building design specification clause: In departments providing intensive care, the HVAC systems are designed so that they continue to operate in a fire emergency. The shutdown panels of these systems are not mentioned in this specifications. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.70 Consideration should be given to subdividing the operating department to enable local transfer of patients from the immediate threat to a temporary place of safety; this could be achieved by: a. sub-compartmenting the operating department with 30 minutes' fire resistance; or b. installing life safety sprinklers (see paragraphs 5.75-C5.96) and dividing the operating department with smokeretarding construction.-Building design specification clause: Considering protecting both patients transfer and healthcare facilities, the sub-compartment of the operating department is designed for at least 30 minutes fire resistance. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.70 Consideration should be given to subdividing the operating department to enable local transfer of patients from the immediate threat to a temporary place of safety; this could be achieved by: a. sub-compartmenting the operating department with 30 minutes' fire resistance; or b. installing life safety sprinklers (see paragraphs 5.75-C5.96) and dividing the operating department with smokeretarding construction.-Building design specification clause: Considering protecting both patients transfer and healthcare facilities, the sub-compartment of the operating department is not required of fire resistance. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.74 In hospitals, electrical distribution is generally provided by essential and nonessential electrical circuits. To enable services to be maintained, the essential circuits are provided with standby generators that operate when there is a failure of mains electricity serving the site or building. These are designed to provide an emergency electrical back-up supply within 15 seconds of a mains failure.-Building design specification clause: Electrical distribution is generally provided by essential and non-essential electrical circuits. The essential circuits are provided with standby generators that operate when there is a failure of mains electricity serving the site or building. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.74 In hospitals, electrical distribution is generally provided by essential and nonessential electrical circuits. To enable services to be maintained, the essential circuits are provided with standby generators that operate when there is a failure of mains electricity serving the site or building. These are designed to provide an emergency electrical back-up supply within 15 seconds of a mains failure.-Building design specification clause: Electrical distribution is generally provided by essential and non-essential electrical circuits. Generators are not provided in this project. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.76 In addition to the above, within each hospital department separate circuits are generally provided for circulation spaces. Therefore, failure of a lighting circuit supplying a circulation space should not affect the lighting circuits in the adjacent rooms, and vice-versa.-Building design specification clause: Within each hospital department separate circuits are generally provided for circulation spaces. Therefore, failure of a lighting circuit suppling a circulation space should not affect the lighting circuits in the adjacent rooms, and vice-versa. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.76 In addition to the above, within each hospital department separate circuits are generally provided for circulation spaces. Therefore, failure of a lighting circuit supplying a circulation space should not affect the lighting circuits in the adjacent rooms, and vice-versa.-Building design specification clause: Within this project separate circuits are not provided for circulation spaces. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.77 While these features provide a degree of resilience, they do not fully address potential failure modes such as final circuit, distribution board or phase failure. Furthermore, HTM 06-01 recommends that emergency escape lighting in all areas can be operational within 0.5 seconds of interruption to the normal supply, which is not achievable solely through the use of standby generators.-Building design specification clause: Emergency escape lighting in all areas can be operational within 0.5 seconds of interruption to the normal supply, which is not achievable solely through the use of standby generators. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.77 While these features provide a degree of resilience, they do not fully address potential failure modes such as final circuit, distribution board or phase failure. Furthermore, HTM 06-01 recommends that emergency escape lighting in all areas can be operational within 0.5 seconds of interruption to the normal supply, which is not achievable solely through the use of standby generators.-Building design specification clause: Emergency escape lighting systems are not included in this project. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.80 All emergency escape lighting should have a minimum duration time of three hours and should incorporate fully automatic network testing facilities.-Building design specification clause: All emergency escape lighting have a duration time of three hours and incorporate fully automatic network testing facilities in this project. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.80 All emergency escape lighting should have a minimum duration time of three hours and should incorporate fully automatic network testing facilities.-Building design specification clause: There is no requirement to emergecny lighting systems in this project. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.81 Where possible, central battery or self contained emergency escape lighting fittings must derive power from essential circuits.-Building design specification clause: Central battery or self contained emergency escape lighting fittings derive power from essential circuts in this project. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.81 Where possible, central battery or self contained emergency escape lighting fittings must derive power from essential circuits.-Building design specification clause: Central battery or self contained emergency escape lighting fittings do not derive power from essential circuts in this project. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.83 The escape route should be clear of obstructions and have a clear height of at least 2 m throughout its length.-Building design specification clause: Each escape route has at least 2 m throughout its length and is clear of obstructions. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.83 The escape route should be clear of obstructions and have a clear height of at least 2 m throughout its length.-Building design specification clause: Each escape route has at least 1.5 m throughout its length and is clear of obstructions. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.84 Where a minimum of two exits are provided, the maximum travel distance from any point within a plantroom should not exceed 25 m to the nearest exit from where alternative means of escape are provided. Of this 25 m, the maximum single direction of escape should not exceed 12 m.-Building design specification clause: The shortest distance from any point within the plantroom to 2 nearest escape exists does not exceed 25 m, of this 25 m, the maximum single direction of escape does not exceed 12 m. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.84 Where a minimum of two exits are provided, the maximum travel distance from any point within a plantroom should not exceed 25 m to the nearest exit from where alternative means of escape are provided. Of this 25 m, the maximum single direction of escape should not exceed 12 m.-Building design specification clause: The shortest distance from any point within the plantroom to 2 nearest escape exists does not exceed 30 m, of this 30 m, the maximum single direction of escape does not exceed 15 m. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.85 Where only one exit is provided, the maximum travel distance should not exceed 12 m.-Building design specification clause: The plantroom has one escape exit in this project, the distance from any point to the exit does not exceed 12m. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.85 Where only one exit is provided, the maximum travel distance should not exceed 12 m.-Building design specification clause: The plantroom has one escape exit in this project, the distance from any point to the exit does not exceed 15m. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.86 Where only one exit is provided, or where there is a danger of people being trapped, alternative means of escape such as ceiling hatches and fixed ladders should be provided.-Building design specification clause: Ceiling hatches and fixed ladders are designed for only one exit set for the plantroom in this project. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.86 Where only one exit is provided, or where there is a danger of people being trapped, alternative means of escape such as ceiling hatches and fixed ladders should be provided.-Building design specification clause: Ceiling hatches and fixed ladders are not provided for only one exit set for the plantroom in this project. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.87 Where the plantroom can be shown to be of very low risk (for example only containing airhandling plant), the distances above may be extended to 25 m and 35 m respectively.-Building design specification clause: The shortest distance from any point within the low risk plantroom to 2 nearest escape exists does not exceed 25 m. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.87 Where the plantroom can be shown to be of very low risk (for example only containing airhandling plant), the distances above may be extended to 25 m and 35 m respectively.-Building design specification clause: The shortest distance from any point within the high risk plantroom to 2 nearest escape exists does not exceed 35 m. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.88 In certain situations it may be essential to maintain a high level of supervision and segregation during an evacuation.-Building design specification clause: Independent evacuation routes are set for infectious patients to maintain segregation and supervision. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 3.88 In certain situations it may be essential to maintain a high level of supervision and segregation during an evacuation.-Building design specification clause: Infectious patients evacuation routes are set together with other people due to project limitations. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.9 For buildings more than one storey in height, all floors should be compartment floors.-Building design specification clause: All floors are compartments floors in this project. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.9 For buildings more than one storey in height, all floors should be compartment floors.-Building design specification clause: Most of floors are compartment floors, there are some exceptions are explained with details in following context. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.11 The maximum area of a compartment should not exceed:• 2000 m2 in a multi-storey building;• 3000 m2 in a single-storey building.-Building design specification clause: The maximum area of a compartment does not exceed 2000 m2 for multi-storey building, and 3000 m2 for single-storey building. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.11 The maximum area of a compartment should not exceed:• 2000 m2 in a multi-storey building;• 3000 m2 in a single-storey building.-Building design specification clause: The maximum area of a compartment exceeds 2000 m2 for multi-storey building, and 3000 m2 for single-storey building as well. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.12 The minimum period of fire resistance (integrity and insulation) provided by compartment walls should be:a. for single-storey healthcare buildings – 30 minutes (except where this conflicts with the requirements of Table 5); orb. for all sprinklered healthcare buildings – 30 minutes; or c. for all other healthcare buildings – 60 minutes, including those with basements more than 10 m deep and those four storeys or more above ground level.-Building design specification clause: The minimum period of fire resistance (integrity and insulation) provided by compartment walls are: a. for single-storey healthcare buildings – 30 minutes (except where this conflicts with the requirements of Table 5); or b. for all sprinklered healthcare buildings – 30 minutes; or c. for all other healthcare buildings – 60 minutes, including those with basements more than 10 m deep and those four storeys or more above ground level. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.12 The minimum period of fire resistance (integrity and insulation) provided by compartment walls should be:a. for single-storey healthcare buildings – 30 minutes (except where this conflicts with the requirements of Table 5); orb. for all sprinklered healthcare buildings – 30 minutes; or c. for all other healthcare buildings – 60 minutes, including those with basements more than 10 m deep and those four storeys or more above ground level.-Building design specification clause: The minimum period of fire resistance (integrity and insulation) provided by compartment walls are not required in this project. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.14 Elements of structure and compartment walls are required to meet the above provisions. Materials used to meet this provision can be found in the Glossary (Appendix A) under “Material of limited combustibility”.-Building design specification clause: All of the elements of structure and compartment walls are required to meet the following minimum period of fire resistance provisions: a. for single-storey healthcare buildings – 30 minutes (except where this conflicts with the requirements of Table 5); or b. for all sprinklered healthcare buildings – 30 minutes; or c. for all other healthcare buildings – 60 minutes, including those with basements more than 10 m deep and those four storeys or more above ground level. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.14 Elements of structure and compartment walls are required to meet the above provisions. Materials used to meet this provision can be found in the Glossary (Appendix A) under “Material of limited combustibility”.-Building design specification clause: All of the elements of structure and compartment walls are not required in this projct. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.15 Where sprinklers are installed throughout the whole building, the requirement for elements of structure and compartment walls to be constructed of materials of limited combustibility does not apply.-Building design specification clause: The requirement for elements of structure and compartment walls to be constructed of materials of limited combustibility does not apply on the place where sprinklers are installed. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.16 All openings in floors and compartment walls should be protected to provide at least the same period of fire resistance as the compartment structure.-Building design specification clause: All openings in floors and compartment walls are protected to provide at least the same period of fire resistance as the compartment structure. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.16 All openings in floors and compartment walls should be protected to provide at least the same period of fire resistance as the compartment structure.-Building design specification clause: All openings in floors and compartment walls are not required fire resistance period. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.18 Compartment walls should be taken up to the underside of the roof covering or deck, and fire-stopped to maintain the fire resistance. The compartment wall should also be continued across any eaves cavity.-Building design specification clause: Compartment walls are taken up to the underside of the roof covering or deck, and fire-stopped to maintain the fire resistance. The compartment wall are continued across any eaves cavity as well. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.18 Compartment walls should be taken up to the underside of the roof covering or deck, and fire-stopped to maintain the fire resistance. The compartment wall should also be continued across any eaves cavity.-Building design specification clause: Compartment walls are taken up to the underside of the roof covering or deck, and fire-stopped do not to maintain the fire resistance. The compartment wall are not continued across any eaves cavity as well. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.19 A zone of the roof 1.5 m wide on either side of the wall should have a covering of designation AA, AB or AC (see Approved Document B, Appendix A, paragraph 6) on a substrate or deck of a material of limited combustibility.-Building design specification clause: Any zone of the roof 1.5 m wide on either side of the wall have a covering of designation AA, AB or AC on a substrate or deck of a material of limited combustibility. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.19 A zone of the roof 1.5 m wide on either side of the wall should have a covering of designation AA, AB or AC (see Approved Document B, Appendix A, paragraph 6) on a substrate or deck of a material of limited combustibility.-Building design specification clause: The covering material of limited combustibility on any zone of the roof 1.5 m wide on either side of the wall are not required. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.22 All openings in sub-compartment walls should be protected to provide a minimum period of fire resistance of 30 minutes.-Building design specification clause: All openings in sub-compartment walls are protected to provide a minimum period of fire resistance of 30 minutes. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.22 All openings in sub-compartment walls should be protected to provide a minimum period of fire resistance of 30 minutes.-Building design specification clause: All openings in sub-compartment walls' fire resistance period is not required. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.23 Uninsulated fire-resisting glazed screens may only be provided in sub-compartment walls provided they satisfy the following requirements: a. the glazing should provide a minimum period of 30 minutes’ fire resistance (integrity only); b. the area of integrity-only glazing should be limited to a maximum of 1 m2 in any room.-Building design specification clause: Uninsulated fire-resisting glazed screens are provided in sub-compartments walls and meet the following requirements: a. the glazing should provide a minimum period of 30 minutes’ fire resistance (integrity only);b. the area of integrity-only glazing should be limited to a maximum of 1 m2 in any room. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.23 Uninsulated fire-resisting glazed screens may only be provided in sub-compartment walls provided they satisfy the following requirements: a. the glazing should provide a minimum period of 30 minutes’ fire resistance (integrity only); b. the area of integrity-only glazing should be limited to a maximum of 1 m2 in any room.-Building design specification clause: Uninsulated fire-resisting glazed screens are not required. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.24 There is no limit on the use of glazed screens that provide a minimum period of fire resistance of 30 minutes (integrity and insulation).-Building design specification clause: Glazed screens in this project provide a minimum period of fire resistance of 30 minutes (integrity and insulation). | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.24 There is no limit on the use of glazed screens that provide a minimum period of fire resistance of 30 minutes (integrity and insulation).-Building design specification clause: Glazed screens in this project are not required for fire resistance period. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.25 Where sprinklers are fitted, there is no limit on the use of glazed screens that provide a minimum period of fire resistance of 30 minutes (integrity only), provided the glass is not of the type referred to as “modified toughened”.-Building design specification clause: The type of glazed screens glass is not referred to as "modified toughened", and the glazed screens provide a minimum period of fire resistance of 30 minutes (integrity only). | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.25 Where sprinklers are fitted, there is no limit on the use of glazed screens that provide a minimum period of fire resistance of 30 minutes (integrity only), provided the glass is not of the type referred to as “modified toughened”.-Building design specification clause: The type of glazed screens glass is not referred to as "modified toughened", and the glazed screens' fire resistance period is not required. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.33 Protected shafts containing a stairway should be provided with an opening window, or similar, providing a clear ventilation area of 1 m2.-Building design specification clause: Protected shafts containing a stairway are provided with an opening window, or similar, providing a clear ventilation area of 1 m2. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.33 Protected shafts containing a stairway should be provided with an opening window, or similar, providing a clear ventilation area of 1 m2.-Building design specification clause: Protected shafts containing a stairway are not provided any window. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.37 Protected lobbies should :a. be constructed from materials of limited combustibility and have the same fire resistance as the protected shaft; and b. contain no other accommodation except that allowed for protected shafts.-Building design specification clause: Protected lobbies in this project :a. are constructed from materials of limited combustibility and have the same fire resistance as the protected shaft; and b. contain no other accommodation except that allowed for protected shafts. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.37 Protected lobbies should :a. be constructed from materials of limited combustibility and have the same fire resistance as the protected shaft; and b. contain no other accommodation except that allowed for protected shafts.-Building design specification clause: Protected lobbies in this project are not made any requirements. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.40 For most building types, it is normally required to protect escape routes with fireresisting walls, ceilings and doors (protected corridors). In healthcare premises this is not considered acceptable, since the excessive number of fire-resisting doors, all fitted with self-closing devices, would be a hindrance to staff and patients during the everyday running of a healthcare building. For this reason, the technique advocated for healthcare buildings is to identify and segregate fire hazard rooms by at least 30 minutes’ fire-resisting construction.-Building design specification clause: In this project, all of the fire hazard rooms are required minimum 30 minutes of fire resistance construction to protect escape routes and daily operation in the building. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.40 For most building types, it is normally required to protect escape routes with fireresisting walls, ceilings and doors (protected corridors). In healthcare premises this is not considered acceptable, since the excessive number of fire-resisting doors, all fitted with self-closing devices, would be a hindrance to staff and patients during the everyday running of a healthcare building. For this reason, the technique advocated for healthcare buildings is to identify and segregate fire hazard rooms by at least 30 minutes’ fire-resisting construction.-Building design specification clause: In this project, all of the fire hazard rooms' fire resistance period is not required. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.46 In the event of a fire, large quantities of smoke and toxic gases can be given off, which potentially could be transferred through the ductwork to rooms and areas remote from the fire. Therefore, measures are required to:a. limit the spread of fire, smoke and other products of combustion within the ductwork between protected areas;b. prevent a breach in the integrity of an enclosing fire-resisting element of construction where penetrated by ductwork.-Building design specification clause: Fire-dampers setting of ductworks between compartments are designed in this project to limit potential hazards from smoke and gas spreading. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.46 In the event of a fire, large quantities of smoke and toxic gases can be given off, which potentially could be transferred through the ductwork to rooms and areas remote from the fire. Therefore, measures are required to:a. limit the spread of fire, smoke and other products of combustion within the ductwork between protected areas;b. prevent a breach in the integrity of an enclosing fire-resisting element of construction where penetrated by ductwork.-Building design specification clause: Fire-dampers setting of ductworks between compartments are not provided in this project. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.49 Ventilation ducts should maintain the period of fire resistance of the construction through which they pass; this includes but is not limited to fire hazard rooms, sub-compartments, compartments, cavity barriers and protected shafts.-Building design specification clause: Ventilation ducts maintain the period of fire resistance of the construction through which they pass; this includes but is not limited to fire hazard rooms, sub-compartments, compartments, cavity barriers and protected shafts. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.49 Ventilation ducts should maintain the period of fire resistance of the construction through which they pass; this includes but is not limited to fire hazard rooms, sub-compartments, compartments, cavity barriers and protected shafts.-Building design specification clause: In thie project, fire resistance period of ventilation ducts is not required. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.68 With the exception of buildings over 30 m in height, the guidance in this document does not require the installation of sprinklers in patient care areas of healthcare buildings. However, the design team is expected to consider the advantages that might be gained by installing life-safety sprinklers throughout the building or to specific areas. Where specific hazards are identified in the building, it may be more appropriate to consider the application of an alternative fire suppression system, such as high pressure water mist technologies.-Building design specification clause: Life-safety sprinklers are designed for specific areas including patient rooms, escape corridors, escape stairways, general doctor's offices etc. in this project. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.68 With the exception of buildings over 30 m in height, the guidance in this document does not require the installation of sprinklers in patient care areas of healthcare buildings. However, the design team is expected to consider the advantages that might be gained by installing life-safety sprinklers throughout the building or to specific areas. Where specific hazards are identified in the building, it may be more appropriate to consider the application of an alternative fire suppression system, such as high pressure water mist technologies.-Building design specification clause: Life-safety sprinklers are not included in this project. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.81 Where pumps are used to draw water from two tanks, each pump should be arranged to draw water from either tank and so that any one pump or either tank could be isolated.-Building design specification clause: Where pumps are used to draw water from two tanks, each pump should be arranged to draw water from either tank and so that any one pump or either tank could be isolated. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.81 Where pumps are used to draw water from two tanks, each pump should be arranged to draw water from either tank and so that any one pump or either tank could be isolated.-Building design specification clause: The systems of pumps and tanks are not included in this project. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.82 The sprinkler water supplies should generally not be used as connections for other services or other fixed fire-fighting systems.-Building design specification clause: The sprinkler water supplies are designed as independent connections for other services or other fixed fire-fighting systems. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.82 The sprinkler water supplies should generally not be used as connections for other services or other fixed fire-fighting systems.-Building design specification clause: The sprinkler water supplies are not designed as independent connections for other services or other fixed fire-fighting systems. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.83 In patient-access areas of healthcare premises, the sprinkler system should be a lifesafety system, fitted with quick-response heads as defined in the Fire Protection Association’s ‘LPC rules for automatic sprinkler installations’-Building design specification clause: In patient-access areas of healthcare premises, the sprinkler system is a lifesafety system, fitted with quick-response heads as defined in the Fire Protection Association’s ‘LPC rules for automatic sprinkler installations’ | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.83 In patient-access areas of healthcare premises, the sprinkler system should be a lifesafety system, fitted with quick-response heads as defined in the Fire Protection Association’s ‘LPC rules for automatic sprinkler installations’-Building design specification clause: In patient-access areas of healthcare premises, the sprinkler system is not included in this project. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.84 Areas of the building not provided with sprinkler protection should be separated from those areas that are protected, by the provision of 60-minute fire-resisting structure (integrity and insulation)-Building design specification clause: Areas of the building not provided with sprinkler protection are separated from those areas that are protected, by the provision of 60-minute fire-resisting structure (integrity and insulation) | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 5.84 Areas of the building not provided with sprinkler protection should be separated from those areas that are protected, by the provision of 60-minute fire-resisting structure (integrity and insulation)-Building design specification clause: Areas of the building not provided with sprinkler protection are separated from those areas that are protected, by the provision of 30-minute fire-resisting structure (integrity and insulation) | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 6.12 Where a roof abuts an external wall, the roof should provide a minimum period of fire resistance of 60 minutes (integrity and insulation) for a distance of 3 m from the wall-Building design specification clause: Where a roof abuts an external wall, the roof provides a minimum period of fire resistance of 60 minutes (integrity and insulation) for a distance of 3 m from the wall | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 6.12 Where a roof abuts an external wall, the roof should provide a minimum period of fire resistance of 60 minutes (integrity and insulation) for a distance of 3 m from the wall-Building design specification clause: Where a roof abuts an external wall, the roof provides a minimum period of fire resistance of 30 minutes (integrity and insulation) for a distance of 3 m from the wall | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 6.16 Buildings or parts of buildings used as parking for cars and other light vehicles are unlike other buildings in certain respects which merit some departure from the usual measures to restrict the fire spread within buildings, specifically:• the fire load is well defined; and • where the car park is well ventilated, there is a low probability of fire spread from one storey to another. Ventilation is the important factor and, as heat and smoke cannot be dissipated so readily from a car park that is not open-sided, fewer concessions are made. The guidance in paragraphs 6.19 to 6.24 below is concerned with three ventilation methods – open-sided (high level of natural ventilation), natural ventilation and mechanical ventilation.-Building design specification clause: Natural ventilation system is designed for car park in this project. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 6.16 Buildings or parts of buildings used as parking for cars and other light vehicles are unlike other buildings in certain respects which merit some departure from the usual measures to restrict the fire spread within buildings, specifically:• the fire load is well defined; and • where the car park is well ventilated, there is a low probability of fire spread from one storey to another. Ventilation is the important factor and, as heat and smoke cannot be dissipated so readily from a car park that is not open-sided, fewer concessions are made. The guidance in paragraphs 6.19 to 6.24 below is concerned with three ventilation methods – open-sided (high level of natural ventilation), natural ventilation and mechanical ventilation.-Building design specification clause: The car park ventilation systems are not include in this project. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 6.22 In most basement car parks, and in enclosed car parks, it may not be possible to obtain the minimum standard of natural ventilation openings set out in paragraph 6.21. In such cases a system of mechanical ventilation should be provided as follows:a. the system should be independent of any other ventilating system (other than any system providing normal ventilation to the car park) and be designed to operate at 10 air changes per hour in a fire condition (see Approved Document F – ‘Ventilation’ for guidance on normal ventilation of car parks);b. the system should be designed to run in two parts, each part capable of extracting 50% of the rates set out in (a) above, and designed so that each part may operate singly or simultaneously;c. each part of the system should have an independent power supply that would operate in the event of failure of the main supply;d. extract points should be arranged so that 50% of the outlets are at high level and 50% at low level;e. the fans should be rated to run at 300°C for a minimum of 60 minutes, and the ductwork and fixings should be constructed of materials having a melting point not less than 800°C.-Building design specification clause: Mechanical ventilation system is designed for basement car park in this project, and the following requirements are met: a. the system is independent of any other ventilating system (other than any system providing normal ventilation to the car park) and be designed to operate at 10 air changes per hour in a fire condition (see Approved Document F – ‘Ventilation’ for guidance on normal ventilation of car parks); b. the system is designed to run in two parts, each part capable of extracting 50% of the rates set out in (a) above, and designed so that each part may operate singly or simultaneously; c. each part of the system has an independent power supply that would operate in the event of failure of the main supply; d. extract points are arranged so that 50% of the outlets are at high level and 50% at low level;e. the fans should be rated to run at 300°C for a minimum of 60 minutes, and the ductwork and fixings are constructed of materials having a melting point not less than 800°C. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 6.22 In most basement car parks, and in enclosed car parks, it may not be possible to obtain the minimum standard of natural ventilation openings set out in paragraph 6.21. In such cases a system of mechanical ventilation should be provided as follows:a. the system should be independent of any other ventilating system (other than any system providing normal ventilation to the car park) and be designed to operate at 10 air changes per hour in a fire condition (see Approved Document F – ‘Ventilation’ for guidance on normal ventilation of car parks);b. the system should be designed to run in two parts, each part capable of extracting 50% of the rates set out in (a) above, and designed so that each part may operate singly or simultaneously;c. each part of the system should have an independent power supply that would operate in the event of failure of the main supply;d. extract points should be arranged so that 50% of the outlets are at high level and 50% at low level;e. the fans should be rated to run at 300°C for a minimum of 60 minutes, and the ductwork and fixings should be constructed of materials having a melting point not less than 800°C.-Building design specification clause: Mechanical ventilation system is designed for basement car park in this project, and there are no more requirements for the ventaliation systems. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 7.3 A minimum of two access points to the site, suitable for use by the fire-and-rescue service, should be provided for fire appliances. Their location should be agreed with all relevant authorities.-Building design specification clause: A minimum of two access points to the site, suitable for use by the fire-and-rescue service, are provided for fire appliances. Their location is agreed with all relevant authorities. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 7.3 A minimum of two access points to the site, suitable for use by the fire-and-rescue service, should be provided for fire appliances. Their location should be agreed with all relevant authorities.-Building design specification clause: A minimum of two access points to the site, suitable for use by the fire-and-rescue service, are provided for fire appliances. Their location will be agreed with all relevant authorities in the future works. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 7.12 If a fire-fighting shaft is required to serve a basement it need not also serve the upper floors unless they also qualify because of the height or size of building. Similarly, a shaft serving upper storeys need not serve a basement that is not large or deep enough to qualify in its own right; however, a fire-fighting stair and any fire-fighting lift should service all intermediate storeys between the highest and lowest storeys that they serve.-Building design specification clause: Each fire-fighting stair and lift services all intermediate storeys bewteen the highest and lowest storeys that they have. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 7.12 If a fire-fighting shaft is required to serve a basement it need not also serve the upper floors unless they also qualify because of the height or size of building. Similarly, a shaft serving upper storeys need not serve a basement that is not large or deep enough to qualify in its own right; however, a fire-fighting stair and any fire-fighting lift should service all intermediate storeys between the highest and lowest storeys that they serve.-Building design specification clause: Fire-fighting stair and lift services requirements are not included in this project. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 7.13 Fire-fighting shafts should serve all floors through which they pass.-Building design specification clause: Fire-fighting shafts serve all floors through which they pass in this project. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 7.13 Fire-fighting shafts should serve all floors through which they pass.-Building design specification clause: Fire-fighting shafts serve most of the floors through which they pass in this project. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 7.14 Fire-fighting stairways and lifts should be approached from inside the building through a fire-fighting lobby.-Building design specification clause: Fire-fighting stairways and lifts are approached from inside the building through a fire-fighting lobby. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 7.14 Fire-fighting stairways and lifts should be approached from inside the building through a fire-fighting lobby.-Building design specification clause: Fire-fighting stairways and lifts are approached from outside of the building. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 7.15 Fire-fighting shafts should be equipped with fire mains having outlet connections and valves in every fire-fighting lobby except at access level.-Building design specification clause: Fire-fighting shafts are equipped with fire mains having outlet connections and valves in every fire-fighting lobby except at access level. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 7.15 Fire-fighting shafts should be equipped with fire mains having outlet connections and valves in every fire-fighting lobby except at access level.-Building design specification clause: Fire-fighting shafts are not required to be equipped with fire mains having outlet connections and valves in every fire-fighting lobby except at access level. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 7.16 Where fire-fighting shafts include firefighting lifts, a fire-fighting lift installation includes:a. the lift car itself; b. the lift well; and c. the lift machinery space together with the lift control system and the lift communications system.-Building design specification clause: A fire-fighting lift installation includes: a. the lift car itself; b. the lift well; and c. the lift machinery space together with the lift control system and the lift communications system. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 7.16 Where fire-fighting shafts include firefighting lifts, a fire-fighting lift installation includes:a. the lift car itself; b. the lift well; and c. the lift machinery space together with the lift control system and the lift communications system.-Building design specification clause: A fire-fighting lift installation includes: a. the lift car itself; b. the lift well. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 7.22 In healthcare premises with a floor over 50 m above ground or access level, wet rising mains should be provided. Where fire mains are provided in healthcare premises that are lower than this, either wet or dry mains are suitable.-Building design specification clause: Wet rising mains are provided for healthcare premises with floors over 50 m. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 7.22 In healthcare premises with a floor over 50 m above ground or access level, wet rising mains should be provided. Where fire mains are provided in healthcare premises that are lower than this, either wet or dry mains are suitable.-Building design specification clause: Wet rising mains are not requied to be provided for healthcare premises with floors over 50 m. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 7.31 In each basement compartment/sub-compartment, the combined cross-sectional area of all smoke outlets should be not less than 2.5% of the compartment/sub-compartment floor area.-Building design specification clause: In each basement compartment/sub-compartment, the minimum combined cross-sectional area of all smoke outlets are higher than 2.5% of the compartment/sub-compartment floor area. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 7.31 In each basement compartment/sub-compartment, the combined cross-sectional area of all smoke outlets should be not less than 2.5% of the compartment/sub-compartment floor area.-Building design specification clause: In each basement compartment/sub-compartment, the minimum combined cross-sectional area of all smoke outlets are higher than 2.0% of the compartment/sub-compartment floor area. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 7.36 The air extraction system should provide at least 10 air changes per hour and be capable of handling gas temperatures of up to 300°C for not less than one hour. It should come into operation automatically on the activation of: a. the sprinkler system; and/or b. the fire detection and alarm system.-Building design specification clause: The air extraction system in this system provides at least 10 air changes per hour and is capable of handling gas temperatures of up to 300°C for not less than one hour. It comes into operation automatically on the activation of: a. the sprinkler system; and/or b. the fire detection and alarm system. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 7.36 The air extraction system should provide at least 10 air changes per hour and be capable of handling gas temperatures of up to 300°C for not less than one hour. It should come into operation automatically on the activation of: a. the sprinkler system; and/or b. the fire detection and alarm system.-Building design specification clause: The air extraction system in this system provides at least 6 air changes per hour and is capable of handling gas temperatures of up to 250°C for not less than one hour. It comes into operation automatically on the activation of: a. the sprinkler system; and/or b. the fire detection and alarm system. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 7.37 Outlet ducts and shafts, including any bulkheads over them, should be enclosed in non-combustible fire-resisting construction.-Building design specification clause: Outlet ducts and shafts, including any bulkheads over them, are enclosed in non-combustible fire-resisting construction. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 7.37 Outlet ducts and shafts, including any bulkheads over them, should be enclosed in non-combustible fire-resisting construction.-Building design specification clause: The material of outlet ducts and shafts, including any bulkheads over them, are not required. | The requirements are not met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 7.38 Where there are natural smoke outlet shafts from different basement compartments of the same basement storey, or from different basement storeys, they should be separated from each other by non-combustible fireresisting construction.-Building design specification clause: Where there are natural smoke outlet shafts from different basement compartments of the same basement storey, or from different basement storeys, they are separated from each other by non-combustible fire-resisting construction. | The requirements are met.
Check if the specification meets the requirement of HTM_05-02_Fire_code.-HTM_05-02_Fire_code: 7.38 Where there are natural smoke outlet shafts from different basement compartments of the same basement storey, or from different basement storeys, they should be separated from each other by non-combustible fireresisting construction.-Building design specification clause: Where there are natural smoke outlet shafts from different basement compartments of the same basement storey, or from different basement storeys, they are not required to be separated from each other by non-combustible fire-resisting construction. | The requirements are not met.